## Slide 1
Presentation July 03, 2003
Technology
PT. INTEGRA TEKNIK ASIA
Engineers Provider - Control and IT-embedded

## Slide 2: Presentation Outline
What is OPC?
Architecture Comparison
History/Background
Microsoft Standard
  OLE, COM, and DCOM
  OLE Automation and ActiveX
Why OPC?
OPC Foundation Working Groups
OPC Architecture Overview
OPC DA
Application Program Interface
Interface to other Standards/Systems
  DCS
  ERP

## Slide 3: What is OPC?
OPC (OLE for Process Control)
Set of standard on Microsoft Windows environment that allow plant-floor data via its own controller and protocol to be accessed by any automation and business process software within Microsoft Windows application
Non-proprietary technical specification, but copyrighted by the OPC Foundation
Set of standard maintained by ‘OPC Foundation’, and based upon Microsoft’s :
  OLE (Object Linking and Embedding) / now ActiveX
  COM (component object model)
  DCOM (distributed component object model) technologies
OPC Technology
Notes: <number>
Everyone's favorite analogy for needing the original Data Access Specification is printer drivers in DOS and then in Windows. Under DOS the developer of each application had to also write a printer driver for every printer. So AutoCAD wrote the AutoCAD application and the printer drivers. And WordPerfect wrote the WordPerfect application and the printer drivers. They had to write a separate printer driver for every printer they wanted to support: one for an Epson FX-80 and one for the H-P LaserJet, and on and on. In the industrial automation world, Intellution wrote their Human Machine Interface (HMI) software and a proprietary driver to each industrial device (including every PLC brand). Rockwell wrote their HMI and a proprietary driver to each industrial device (including every PLC brand, not just their own).
Windows solved the printer driver problem by incorporating printer support into the operating system. Now one printer driver served all the applications! And these were printer drivers that the printer manufacturer wrote (not the application developer). Windows provided the infrastructure to allow the industrial device driver's solution as well. Adding the OPC specification to Microsoft's OLE technology in Windows allowed standardization. Now the industrial devices' manufacturers could write the OPC DA Servers and the software (like HMIs) could become OPC Clients.

## Slide 4: Architecture Comparison
Process
I / O
Comm Protocol
Comm Interface
DDE Server
Protocol Driver
Comm Interface
DDE Clients
Process S/W
Process
I / O
Comm Protocol
Comm Interface
Proprietary I/F
Protocol Driver
Comm Interface
Process S/W
Process
I / O
Comm Protocol
Comm Interface
OPC Server
Protocol Driver
Comm Interface
OPC Clients
Process S/W
Controller Smart Device DCS Sub-System
Computer
OPC Technology

## Slide 5: History / Background
Without any standard :
  Protocol driver is developed by automation software provider for their own-software
  Much duplication of effort, due to each software developer must write a driver for a particular vendor’s hardware
  Hardware manufacturers attempt to developing drivers for their product, but are hindered by differences standard applied in each automation software
With DDE Standard:
  Hardware manufacturers or 3rd party protocol developer use this data exchange standard as an alternative to escape from the proprietary interface, even this DDE standard is not specially design for process control real-time data exchange application
With OPC :
  A simplified, stage-one solution was released in August 1996
  open, flexible, plug-and-play standard that allows end users to enjoy a greater choice of solutions, as well as sharply reducing development and maintenance costs for hardware and software suppliers
OPC Technology
Notes: <number>
OLE for Process Control Date: August 29, 1996.
Requires Windows 95 or Windows NT 3.51 or later for in process servers.
Requires Windows NT 4.0 or later for local or remote servers.
The document includes both an OLE automation interface and a custom COM interface (COM extension library).

## Slide 6: COM/DCOM and OLE
COM enables the definition of standard objects, methods, and properties for servers of real-time information
COM is generic and is the core of DCOM, ActiveX, and OLE technology
DCOM extends COM to networks (remote objects), highly optimized protocol, where remote components appear to be local
OLE is used to/for :
  provide integration among applications
  enabling a high degree of application compatibility
  allows for the development of reusable, plug-and-play objects
  interoperable across multiple applications
OPC Technology

## Slide 7: OLE Automation and ActiveX
OLE Automation and the underlying COM technologies were designed by Microsoft to allow components (written in C and C++) to be used by a custom program (written in Visual Basic or Delphi)
COM is generic and is the core of DCOM, ActiveX, and OLE technology
ActiveX is an umbrella term of a broad range of technologies that used to be known as OLE Controls, all of which rely on COM. A renaming and restructuring of the OLE Controls technology, it is object-based rather than object-oriented
OPC Technology
Notes: <number>
OPC interfaces implemented using Microsoft’s ActiveX Template Library (ATL). ATL is the best way to do COM programming

## Slide 8: Why OPC?
Open Connectivity
  provide common access to industrial plant floor data
  free to choose from a wider variety of plant floor devices and automation software
Easy to Use
  browse and select object
  reduce time on solving connectivity issue
Open Space for Software Developer and Hardware Manufacturers
  wide-range of OPC Server
  modular OPC Clients
  hundreds developers member
OPC Technology
Notes: <number>
OPC Provides Industry-Standard Connectivity and Interoperability
The vision of OPC is to be the foundation for
INTEROPERABILITY for moving information vertically from the factory floor through the enterprise of multi-vendor systems
INTEROPERABILITY between devices on different industrial networks from different vendors
OPC is open connectivity in industrial automation and the enterprise systems that support industry. Interoperability is assured through the creation and maintenance of open standards specifications. There are currently seven standards specifications completed or in development

## Slide 9: OPC Foundation Working Groups
OPC DA (Data Access)
OPC AE (Alarms and Events)
OPC HDA (Historical Data Access)
OPC DX (Data eXchange)
OPC XDA (XML Data Access)
OPC Security
OPC Batch, based-on IEC 61512-1
OPC Commands
OPC Common I/O, based on IEC 61131-3
OPC Complex Data
OPC Compliance
OPC Technology
Notes: <number>
OPC Data Access The originals! Used to move real-time data from PLCs, DCSs, and other control devices to HMIs and other display clients. The Data Access 3 specification is now a Release Candidate. It leverages earlier versions while improving the browsing capabilities and incorporating XML-DA Schema.
OPC Alarms & Events Provides alarm and event notifications on demand (in contrast to the continuous data flow of Data Access). These include process alarms, operator actions, informational messages, and tracking/auditing messages.
OPC Batch This spec carries the OPC philosophy to the specialized needs of batch processes. It provides interfaces for the exchange of equipment capabilities (corresponding to the S88.01 Physical Model) and current operating conditions.
OPC Data eXchange This emerging specification takes us from client/server to server-to-server with communication across Ethernet fieldbus networks. This provides multi-vendor interoperability! And, oh by the way, adds remote configuration, diagnostic and monitoring/management services.
OPC Historical Data Access Where OPC Data Access provides access to real-time, continually changing data, OPC Historical Data Access provides access to data already stored. From a simple serial data logging system to a complex SCADA system, historical archives can be retrieved in a uniform manner.
OPC Security All the OPC servers provide information that is valuable to the enterprise and if improperly updated, could have significant consequences to plant processes. OPC Security specifies how to control client access to these servers in order to protect this sensitive information and to guard against unauthorized modification of process parameters.
OPC XML-DA This specification is being developed to provide flexible, consistent rules and formats for exposing plant floor data using XML, leveraging the work done by Microsoft and others on BizTalk, SOAP, and other XML frameworks.
OPC Commands A Working Group has been formed to develop a new set of interfaces that allow OPC clients and servers to identify, send and monitor control commands which execute on a device.
OPC Common I/O The Working Group is determining the need for a separate specification to address the needs of soft control functions like initialization and shutdown. There are also Working Groups for Compliance and Demos, but their deliverables are not specifications.

## Slide 10: Architecture Overview
Process
I / O
Comm Protocol
Comm Interface
OPC Server DA/AE/HDA/DX
Protocol Driver
Comm Interface
Controller Smart Device DCS Sub-System
Computer
Process
I / O
Comm Protocol
Comm Interface
DX
OPC DA Clients
RealTime PV
OPC AE Clients
Alarm/Event SP
OPC HDA Clients
Historian DB
OPC Server DA/AE/HDA/DX
Protocol Driver
Comm Interface
HDA
AE
DA
HDA
AE
DA
OPC Technology

## Slide 11: OPC DA Server
COM Object Hierarchy
OPCServer
OPCGroups (collection)
OPCGroup
OPCItems (collection)
OPCItem
OPCBrowser
OPC Technology

## Slide 12: OPC DA Server 2.0
“Server” COM object
  IOPCServer
  IOPCBrowseServerAddressSpace
  IOPCCommon
  IOPCItemProperties
  IConnectionPointContainer
“Group” COM object
  IOPCGroupStateMgt
  IOPCAsyncIO2
  IOPCItemMgt
  IOPCSyncIO
  IConnectionPointContainer
OPCServer
OPCGroup
OPC Technology

## Slide 13: OPC DA Client 2.0
Client provides two (2) COM interfaces that the server can call :
IOPCShutdown
IOPCDataCallback
Server Object
Group Object(s)
Client
IOPCDataChange
IOPCShutdown
OPC Technology

## Slide 14: Interfaces and Registry
Interface
  OPC server developers must implement all functionality of required interfaces
  OPC client communicates to an OPC server by calling functions from the OPC required interfaces
Installation and Registration
  each OPC Server must register itself with the Component Categories Manager, a Microsoft supplied system COM object
  a server should first register the OPC defined Category ID (CATID) and the OPC defined Category Description, and then register its own CLSID
  OPC Clients will query the Components Category Manager to enumerate the CLSIDs of all registered OPC Servers
  Clients will use the Interface IOPCServerList to obtain a list of servers either locally or on a remote host
OPC Technology
Notes: <number>
register the OPC defined Category ID (CATID) and the OPC defined Category Description by calling ICatRegister:RegisterCategories()
register its own CLSID as an implementation of the CATID with a call to ICatRegister:: RegisterClassImplCategories()

## Slide 15: Application Program Interface
OPC Automation
Wrapper
C++ Application
VB Application
OPC Automation Inf.
OPC Custom Interface
OPC Server
Local or Remote
(shared by many Clients)
Server Data Cache
I/O data
Device
OPC Technology
Notes: <number>
Understanding of Microsoft Foundation Classes (MFC) and WIN32 programming is required.

## Slide 16: Interface to other Standard
OPC Server
Other Standard
OPC Standard
OPC Client
ODBC Interface
OPC Client
DDE Client
OPC Client
xyz client/inf
DDE Server
xyz
OPC Technology

## Slide 17: Interface to DCS
Bailey Infi/Net 90
OPC Server
Open environment
Proprietary
C I U
E W S
Bailey PlantLoop Bailey Central-Net (proprietary network and protocol)
P C U
P C U
I/O
I/O
MOD300
Multibus
ABB MOD300
OPC Server
Distributed Communication Network (proprietary protocol)
OPC Server
DeltaV
Redundant Ethernet (proprietary protocol)
OPC Technology

## Slide 18: Interface to ERP
OPC Technology

## Slide 19: Interface to ERP
OPC Technology

## Slide 20: OPC Interoperability Exhibition Integra Teknik Asia www.integrateknik.com
GE Fanuc
Intellution iFix
MMI
CiTect
MMI
Wonderware
InTouch
MMI
RS-232
Multi Ports/Protocols
Controller w/ IEC 61131-3
Ethernet
RS-232
RS-485
RS-232
R T U
w/ IEC 60870-5-101
Protocol
RS-485
Digital Power
Transducer
IEDs (Intelligent
Electronic Devices)
Modbus
Vortex
ESP
Controller
RS-485
Keltronics
ESP
Controller
RS-485
IEC-101
Multi-protocols on single channel
DCOM on Ethernet 10/100Mbps
Excel w/
OPC Add-In
MySQL
OPC-ODBC
IEC
60870-5-104
Modbus
TCP/IP
CAN
bus
Modbus
ASCII
Protocols Scanner/Driver with Specific scan-algorithm for devices in-template
Hybrid Multi OPC Server
with Template Devices (auto-tags generation)
Ethernet
Serial RS-232 / RS-422 / RS-485
IEC
60870-5-101
IEC
60870-5-103
Modbus
RTU
Modbus
RS-232
Component Object Module interface
DNP3.0
Digital
Power
Meter
RS-485
Integrated
Controller/LCD

## Slide 21
OPC Technology OPEN Discussion
OPC Technology/Concept
OPC Application
  SCADA
  DCS
  ERP
OPC Server
OPC Client
OPC Variant
  OPC on UNIX
  OPC at Embedded Controller
  OPC - DDE
  OPC - ODBC
Notes: <number>

## Slide 22: End of OPC Presentation July 03, 2003
Thank you for your kind attention and active participation
PT. INTEGRA TEKNIK ASIA
Engineers Provider - Control and IT-embedded
Notes: <number>